## Sheet1
Water-Based Fire Protection System Inspection Guidelines for Tagging - 2011 NFPA 25
Inspecton Deficiencies, Testing Deficiencies, Maintenance Deficiencies (Revised 12-5-2014)
Item | Deficiency | Tag | NFPA | Action | Reference
FOAM-WATER SPRINKLER SYSTEM |  |  |  |  | NFPA #25
Alarm devices/waterflow devices | Physical damage apparent | Red | Noncritical | 30 day notice | 11.1.4.1.1 11.1.4.1.2 11.1.4.1.3
Pipe and fittings | Mechanical damage, missing or damaged paint or coating, rusted or corroded, not properly alligned or trapped sections, low point drains not functioning, improper location or poor condition of rubber-gasketed fittings | Red | Critical | 30 day notice | 11.2.3
Hangers & seisic braces | Damaged or missing, not securely attached to strutural or piping, missing or damaged paint or coating, rusted or corroded. | Red | Noncritical | 30 day notice | 11.2.4
Foam-water discharge devices | Discharge devices missing, not properly positioned or pointed in design direction, loaded or corroded | Red | Critical | 24 hour notice | 11.2.5.1
| Caps and plugs not free to operate as intended. | Red | Critical | 30 day notice | 11.2.5.2
| Missing caps or plugs | Red | Noncritical | 30 day notice | 11.2.5.2
| Discharge devices not listed for use with foam concentrate | Red | Critical | 30 day notice | 11.2.5.4
Mainline and/or discharge device strainers | Baskets or screens damaged or not clean | Red |  | 30 day notice | 11.2.7.1
Foam concentrate strainers | Blow-down valve open or not plugged | Red | Critical | 24 hour notice | 11.2.7.2
Drainage | Trap sumps and drainage trenches blocked, retention embankments or dikes in disrepair | Red | Noncritical | 30 day notice | 11.2.8
Proportioning systems (all) | Proportioning system valves not in correct open/closed position in accordance with specified operating conditions | Red | Impairment | 24 hour notice | 11.2.9.3
| Concentrate tank does not have correct quantity required by original design | Red | Critical | 30 day notice (24 hour notice if no reserve supply) | 11.2.9.4
Standard pressure proportioner | Automatic drains (ball drip valves) not free or open, external corrosion on foam concentrate tanks | Red | Noncritical | 30 day notice | 11.2.9.5.1
| Ball drip drain valves not cleaned within last 5 years | Red |  | 30 day notice | 11.4.3.1
| Foam liquid storage tank not flushed within last 10 years | Red |  | 30 day notice | 11.4.3.2
Bladder tank proportioner | Water control valve to foam concentrate in "closed" position | Red | Impairment | 24 hour notice | 11.2.9.5.2
Bladder tank proportioner | Foam in water surrounding bladder | Red | Critical | 24 hour notice | 11.2.9.5.2
Bladder tank proportioner | External corrosion on foam concentrate tank | Red | Noncritical | 30 day notice | 11.2.9.5.2
Bladder tank proportioner | Sight glass not cleaned within last 10 years | Red |  | 30 day notice | 11.4.4.1
Line proportioner | Strainer damaged, corroded, plugged or fouled, pressure vacuum vent not operating freely | Red | Critical | 24 hour notice | 11.2.9.5.3
Line proportioner | External corrosion on foam concentrate tank | Red | Noncritical | 30 day notice | 11.2.9.5.3
Line proportioner | Foam liquid storage tank not flushed within last 10 years | Red |  | 30 day notice | 11.4.5.2
| Foam liquid storage tank not internally inspected within last 10 years | Red |  | 30 day notice | 11.4.5.1
Standard balanced pressure proportioner | Sensing line valves not open, no power to foam liquid pump | Red | Impairment | 24 hour notice | 11.2.9.5.4
Standard balanced pressure proportioner | Stainer damaged, corroded, plugged, or fouled, pressure vaccum vent not operating freely, gauges damaged or not showing proper pressures | Red | Critical | 24 hour notice | 11.2.9.5.4
Standard balanced pressure proportioner | Foam concentrate pump not operated and foam circulated within the last 5 years | Red |  | 30 day notice | 11.4.6.1
Standard balanced pressure proportioner | Foam pumps, drive train and drivers not serviced within the last 5 years | Red |  | 30 day notice | 11.4.6.2
Standard balanced pressure proportioner | Diaphragm balancing valve not flushed within the last 5 years | Red |  | 30 day notice | 11.4.6.3
Standard balanced pressure proportioner | Foam concentrate tank not internally inspected for corrosion within the last 10 years | Red |  | 30 day notice | 11.4.6.4
In-Line balanced pressure proportioner | Sensing line valves at pump unit or individual proportioner stations not open, no power to foam liquid pump | Red | Impairment | 24 hour notice | 11.2.9.5.5
In-Line balanced pressure proportioner | Stainer damaged, corroded, plugged, or fouled, pressure vaccum vent not operating freely, gauges damaged or not showing proper pressures | Red | Critical | 24 hour notice | 11.2.9.5.5
In-Line balanced pressure proportioner | Foam concentrate pump not operated and foam circulated within the last 5 years | Red |  | 30 day notice | 11.4.7.1
In-Line balanced pressure proportioner | Foam pumps, drive train and drivers not serviced within the last 5 years | Red |  | 30 day notice | 11.4.7.2
In-Line balanced pressure proportioner | Diaphragm balancing valve not flushed within the last 5 years | Red |  | 30 day notice | 11.4.7.3
In-Line balanced pressure proportioner | Foam concentrate tank not internally inspected for corrosion within the last 10 years | Red |  | 30 day notice | 11.4.7.4
Pressure vacuum vents | Not flushed and serviced within the last 5 years | Red |  | 30 day notice | 11.4.8
Orifice plate proportioner | No power to foam liquid pump | Red | Impairment | 24 hour notice | 11.2.9.5.6
Orifice plate proportioner | Stainer damaged, corroded, plugged, or fouled, pressure vaccum vent not operating freely, gauges damaged or not showing proper pressures | Red | Critical | 24 hour notice | 11.2.9.5.6
Foam concentrate | Samples not taken and submitted for test | Red | Critical | 30 day notice | 11.2.10
Automatic detection equipment | Missing detectors, loose, not protected from corrosion or weather, damaged, communication wiring, control panels or pneumatic tubing system non functional | Red |  | 24 hour notice | NFPA #72
Alarm devices | Water motor and gong not functioning | Red | Critical | 30 day notice | 11.3.1.1
Alarm devices | Pressure switch or vane type switch not functioning or no alarm | Red | Critical | 30 day notice | 11.3.1.2
Operational Test | Fire detection system did not operate within requirements of NFPA #72 | Red | Critical | 24 hour notice | 11.2.3.4
Operational Test | Test not done after 1 year | Red | Noncritical | 30 day notice | 11.3 Table 11.1
Operational Test | Nozzles are plugged | Red | Impairment | 24 hour notice | 11.3.2.6.1
Operational Test | Nozzles are not correctly positioned |  | Critical | 30 day notice | 11.3.2.6.1
Operational Test | Pressure readings are not comparable to original design requirements | Red | Critical | 24 hour notice | 11.3.2.7.3
Operational Test | Test not performed with maximum number of systems expected to operate | Red |  | 30 day notice | 11.3.3
Operational Test | Manual actuation devices did not work properly | Red | Impairment | 24 hour notice | 11.3.4
Operational Test | Foam sample did not pass concentration test | Red | Impairment | 24 hour notice | 11.3.5.3
Standard pressure proportioner | Foam liquid storage tank not internally inspected or hydrostatically tested within the last 10 years | Red |  | 30 day notice | 11.4.3.3
Bladder tank proportioner | Foam concentrate tank not hydrostatically tested within last 10 years | Red |  | 30 day notice | 11.4.4.2
Main drain | 10% or more drop in full flow pressure or slow return to normal static pressure. | Red | Impairment | 24 hour notice | 13.2.5.2
Obstruction inspection | No inspection of main and branch line after 5 years or inspection revealed presence of MIC, zebra mussels, rust and scale | Red | Critical | 30 day notice | 14.2.1
WATER SPRAY FIXED SYSTEMS |  |  |  |  | NFPA #25
Pipe and fittings | Mechanical damage, missing or damaged paint or coating, rusted or corroded, not properly alligned or trapped sections, low point drains not functioning, improper location of rubber-gasketed fittings | Red | Critical | 30 day notice | 10.2.4.1
Hangers & seismic braces | Damaged or missing, not securely attached to structural or piping, missing or damaged paint or coating, rusted or corroded. | Red | Noncritical | 30 day notice | 10.2.4.2
Water spray nozzles | Discharge devices missing, not properly positioned or pointed in design direction, loaded or corroded | Red | Critical | 24 hour notice | 10.2.5.1
Water spray nozzles | Missing caps or plugs if required or not free to operate as intended. | Red | Critical | 30 day notice | 10.2.5.2
Mainline strainers and individual water spray nozzle strainer | Strainer plugged or fouled | Red | Impairment | 24 hour notice | 10.2.7
Mainline strainers and individual water spray nozzle strainer | Strainer damaged or corroded | Red | Noncritical | 30 day notice | 10.2.7
Drainage | Trap sumps and drainage trenches blocked, retention embankments or dikes in disrepair | Red | Noncritical | 30 day notice | 10.2.8
Automatic detection equipment | Missing detectors, loose, not protected from corrosion or weather, damaged, communication wiring, control panels or pneumatic tubing system non functional | Red |  | 24 hour notice | NFPA #72
Ultra-High-Speed | Detectors have physical damage or deposits on lenses of optical detectors | Red | Critical | 24 hour notice | 10.4.2
Ultra-High-Speed | Controllers found to have faults | Red | Critical | 24 hour notice | 10.4.3
Operational test | Heat detection system did not operate within 40 seconds, flammable gas detection system did not operate within the time frame specifiecd in system design | Red | Critical | 24 hour notice | 10.3.4.1
Operational test | Test not done after 1 year | Red | Noncritical | 30 day notice | 10.3.4.1
Operational test | Nozzles are plugged | Red | Impairment | 24 hour notice | 10.3.4.3.1
Operational test | Nozzles not correctly positioned | Red | Critical | 30 day notice | 10.3.4.3.1
Operational test | Pressure readings are not comparable to original design requirements | Red | Critical | 24 hour notice | 10.3.4.4
Operational test | Test not performed with maximum number of systems expected to operate | Red |  | 30 day notice | 10.3.5
Operational test | Manual actuation devices did not work properly | Red | Impairment | 24 hour notice | 10.3.6
Low point drains/weep holes | Piping not drained, weep holes not clear or obstructed | Red |  | 30 day notice | 10.3.7.2
Ultra-High-Speed Operational test | Response time was more than 100 milliseconds | Red | Impairment | 24 hour notice | 10.4.5
Ultra-High-Speed Operational test | Test not done after 1 year | Red | Noncritical | 30 day notice | 10.4.1
Main drain | 10% or more drop in full flow pressure or slow return to normal static pressure. | Red | Impairment | 24 hour notice | 10.3.7.1
Obstruction inspection | No inspection of main and branch line after 5 years or inspection revealed presence of MIC, zebra mussels, rust and scale | Red | Critical | 30 day notice | 14.2.1