## Sheet1
Water-Based Fire Protection System Inspection Guidelines for Tagging - 2011 NFPA 25
Testing Deficiencies and Maintenance Deficiencies (Revised 12-5-2014)
Item | Deficiency |  | NFPA | Action | Reference
SPRINKLER SYSTEMS |  |  |  |  | NFPA #25
Sprinklers - standard | No test after 50 years, every 10 years thereafter | Red | Noncritical | 30 day notice | 5.3.1.1.1
standard | Prior to 1920 not replaced | Red | Critical | 30 day notice | 5.3.1.1.1.2
standard | No test after 75 years, every 5 years thereafter | Red | Noncritical | 30 day notice | 5.3.1.1.1.5
Solder-type 325° or greater | No test after 5 years, every 5 years thereafter | Red | Noncritical | 30 day notice | 5.3.1.1.1.4
fast response | No test after 20 years, every 10 years thereafter | Red | Noncritical | 30 day notice | 5.3.1.1.1.3
dry | No test after 10 years, every 10 years thereafter | Red | Critical | 30 day notice | 5.3.1.1.1.6
Subject to harsh environments | (Corrosive atmospheres, corrosive water supply, includes freezers and coolers) No test after 5 years, every 5 years thereafter | Red | Noncritical | 30 day notice | 5.3.1.1.2
Solder type | (Commercial-type cooking eqpt. & ventilating systems) No replacement after one year | Red | Critical | 24 hour notice | 5.4.1.9
Sprinklers in spray coating areas | Not protected or plastic or paper bags used to protect against overspray residue, with deposits or residue accumulation | Red | Impairment | 24 hour notice | 5.4.1.7.1 5.4.1.7.2
Gauges | Not replaced or calibrated in 5 years, not accurate within 3% of scale | Red | Noncritical | 30 day notice | 5.3.2
Alarm devices | Water motor and gong not functioning | Red | Critical | 30 day notice | 5.3.3
Alarm devices | Pressure switch or vane type switch not functioning or no alarm | Red | Critical | 24 hour notice | 5.3.3
Antifreeze systems | Specific gravity of antifreeze not correct | Red | Critical | 30 day notice | 5.3.4
Main drain | 10% or more drop in full flow pressure or slow return to normal static pressure. | Red | Impairment | 24 hour notice | 13.2.5.2
Obstruction inspection | No inspection of main and branch line after 5 years or inspection revealed presence of MIC, zebra mussels, rust and scale | Red | Critical | 30 day notice | 14.2.1
VALVE, COMPONENTS & TRIM |  |  |  |  | NFPA #25
Control valve | Valve will not operate through its full range | Red | Critical | 24 hour notice | 13.3.3.1
Control valve | No spring or torsion felt in rod when opening post indicator valve | Red | Impairment | 24 hour notice | 13.3.3.2
Supervisory switches (Valve not locked or sealed) | No signal from two revolutions of the hand wheel from normal position or when stem has moved one-fifth of the distance from normal position, signal restored in position other than normal | Red | Critical | 24 hour notice | 13.3.3.5.2 13.3.3.5.3
Supervisory switches (Valve locked or sealed) | No signal from two revolutions of the hand wheel from normal position or when stem has moved one-fifth of the distance from normal position, signal restored in position other than normal | Red | Noncritical | 30 day notice | 13.3.3.5.2 13.3.3.5.3
Preaction valve and deluge valve | Priming water level not correct | Red | Critical | 30 day notice | 13.4.3.2.1
Deluge valve | Annual full flow trip test revealed plugged nozzles, pressure reading at hydraulically most remote nozzle and/or at valve not comparible to original design values, manual actuation devices did not operate properly | Red | Impairment | 24 hour notice | 13.4.3.2.2.3 13.4.3.2.7.3 13.4.3.2.9
Preaction valve and deluge valve | Low air pressure switch did not send signal or no alarm | Red | Noncritical | 30 day notice | 13.4.3.2.13
Preaction valve and deluge valve | Low temperature switch did not send signal or no alarm | Red | Noncritical | 30 day notice | 12.4.3.2.14
Preaction valve and deluge valve | Automatic air maintenance device did not pass test | Red | Noncritical | 30 day notice | 13.4.3.2.15
Preaction valve and deluge valve | No full flow trip test done after 3 years or test results not comparable to previous results or within water delivery table limits if applicable | Red | Noncritical | 30 day notice | 13.4.3.2.2.4 13.4.3.2.3 13.4.3.2.7.3
Preaction valve | No air leakage test after 3 years | Red | Noncritical | 30 day notice | 13.4.3.2.6
Preaction valve | Three year air leakage test failed | Red | Critical | 30 day notice | 13.4.3.2.6
Dry pipe valve/Quick opening device | Priming water level not correct | Red | Critical | 30 day notice | 13.4.4.2.1
Dry pipe valve | Annual trip test results were not comparible to previous tests | Red | Noncritical | 30 day notice | 13.4.4.2.2
Dry pipe valve | No full flow tripi test done after 3 years or test results not comparable to previous tests | Red | Noncritical | 30 day notice | 13.4.4.2.2.2
Dry pipe valve | Quick opening device did not pass test | Red | Critical | 24 hour notice | 13.4.4.2.4
Dry pipe valve | Low air pressure switch did not send signal or no alarm | Red | Noncritical | 30 day notice | 13.4.4.2.6
Dry pipe valve | Low temperature switch did not send signal or no alarm | Red | Noncritical | 30 day notice | 13.4.4.2.7
Dry pipe valve | Automatic air maintenance device did not pass test | Red | Critical | 24 hour notice | 13.4.4.2.8
| Trip test tag or card missing | Red |  | 30 day notice | 13.4.4.2.5
Dry pipe valve | No air leakage test after 3 years | Red | Noncritical | 30 day notice | 13.4.4.2.9
Dry pipe valve | Three year air leakage test failed | Red | Critical | 30 day notice | 13.4.4.2.9
Sprinkler pressure reducing control valves | No full flow test done after 5 years or test results not comparable to previous results | Red | Noncritical | 30 day notice | 13.4.3.2.3
PRIVATE FIRE SERVICE MAINS |  |  |  |  | NFPA #25
Underground and exposed piping | No flow test done after 5 years or test results not comparable to previous results | Red | Noncritical | 30 day notice | 7.3.1
Backflow prevention assemblies | Did not pass forward flow test | Red | Impairment | 24 hour notice | 13.6.2.1
Backflow prevention assemblies | No forward flow test done after one year | Red | Noncritical | 30 day notice | 13.6.2.1
Backflow prevention assemblies | Did not pass backflow performance test | Red | Noncritical | 30 day notice | 13.6.2.1
Dry barrel & wall hydrant | Hydrant did not flow clear or did not drain within 60 minutes | Red | Noncritical | 30 day notice | 7.3.2.1 7.3.2.4
Monitor nozzles | Did not flow acceptable amount of water or did not operate throughout their full range | Red | Critical | 24 hour notice | 7.3.3.1 7.3.3.2
STANDPIPE & HOSE SYSTEM |  |  |  |  | NFPA #25
Master pressure reducing valve | Partial flow test not performed or test failed | Red |  | 30 day notice | 13.5.4.2
Master pressure reducing valve | Full flow test not performed or test results not comparable to previous test results | Red |  | 30 day notice | 13.5.4.3
Hose connection pressure reducing valves | No full flow test done after 5 years or test results not comparable to previous results | Red | Noncritical | 30 day notice | 13.5.3.2
Hose rack assembly pressure reducing valve | No full flow test done after 5 years or test results not comparable to previous results | Red | Noncritical | 30 day notice | 13.5.3.2
Hose valves (Class I and Class III standpipe system) | Annual test revealed valve leaking or difficult to operate | Red | Critical | 30 day notice | 13.5.6.2.1 13.5.6.2.1.1
Hose valves (Class II standpipe system) | Test revealed valve leaking or difficult to operate | Red | Critical | 30 day notice | 13.5.6.2.2
Hose valves (Class II standpipe system) | No test after 3 years | Red | Noncritical | 30 day notice | 13.5.6.2.2
Hose | No test after initial 5 years or 3 years thereafter or did not pass service test | Red |  | 30 day notice | 6.2.1 NFPA #1962
Hose nozzle | Waterway obstructed, tip damaged, controls and adjustments do not operate as designed, shutoff valve if provided does not operate as designed or close off flow completely | Red |  | 30 day notice | 6.2.1 NFPA #1962
Hose storage device | Rack will not swing out of cabinet at least 90° | Red | Noncritical | 30 day notice | 6.2.1
Main drain | 10% or more drop in full flow pressure or slow return to normal static pressure. | Red | Critical | 24 hour notice | 6.3.1.5 13..2.5.2
Standpipe system | Test results did not provide design pressure at required flow | Red | Critical | 24 hour notice | 6.3.1.1
Standpipe system | No flow test done after 5 years | Red | Noncritical | 30 day notice | 6.3.1.1
Manual standpipe system and semi-automatic dry standpipe systems including FDC piping | Hydrostatic test showed leaks | Red | Critical | 24 hour notice | 6.3.2.1
| No hydrostatic test done after 5 years | Red | Noncritical | 30 day notice | 6.3.2.1
Gauges | Not replaced or calibrated in 5 years, not accurate within 3% of scale | Red | Noncritical | 30 day notice | 6.3.4
Obstruction inspection | No inspection of main and branch line after 5 years or inspection revealed presence of MIC, zebra mussels, rust and scale | Red | Critical | 30 day notice | 14.2.1