## Slide 1
Florida Fire Marshal Rules
69A-46 Revisions – 2016
WATER BASED FIRE PROTECTION SYSTEMS
June, 2016

## Slide 2
The 69A-46 Revisions are the result of the Industry efforts over several years with the cooperation of the Fire Marshal’s Office. Authorities Having Jurisdiction, Florida Fire Sprinkler Association and Florida Chapter of the American Fire Sprinkler Association all participated. The Revisions were reviewed by the Fire Marshal’s Office, Legal Staff and available through a Workshop and Posting for Public comment.
Revisions were needed as follows:
1. The tagging requirements went into effect in 2008 and with usage, it became clear that both Sprinkler Contractors and AHJ’s needed further clarification and direction
2. Create greater consistency in application by Sprinkler Contractors and AHJ’s.
3. Desire to match new NFPA terms and classifications
4. Help address liability concerns
FIRE MARSHAL RULES

## Slide 3: FIRE MARSHAL RULES
69A-46.0165 Submission of the Application for a Water-Based Fire Protection Inspector Permit.
(8) A Water-Based Fire Protection Inspector permittee must qualify and maintain a NICET Level II or equivalent certification in a subfield of Inspection and Testing of Water-Based Systems as a condition to renewal.
Basis of Revision:
In 2012, paragraph 4 was revised to allow equivalent education and training approved by the State Fire Marshal. The Sprinkler Academy has such a program approved. However, the equivalent was not included for the renewal process.

## Slide 4: FIRE MARSHAL RULES
69A-46.017 Required Continuing Education.
(6)(f) Examples of courses which will be approved if the criteria and procedures of this rule are met: 1. Florida Fire Sprinkler Association training and seminars;
2. American Fire Sprinkler Association trainings and seminars;
3. NFPA seminars and;
Basis of Revision:
The rule now recognizes the training and seminars that were being approved by the State Fire Marshal’s Office for CEU’s.
(10) Paragraph deleted
Basis of Revision:
The requirements for CEU’s were added in 2008 and specific dates were referenced which have now passed so paragraph is no longer relevant or needed.

## Slide 5: FIRE MARSHAL RULES
69A-46.030 Definitions.
(1) The definitions provided in Section 633.102, F.S., shall also apply to this rule chapter.
Basis of Revision:
This revision was made by the Fire Marshal’s Office
(3) Deficiency. For the purposes of inspection, testing, and maintenance of a water-based fire protection system, a condition that will or has the potential to adversely impact the performance of a system or portion thereof but does not rise to the level of an impairment.
(a) Critical Deficiency. A deficiency that, if not corrected, can have a material effect on the ability of the fire protection system or unit to function as intended in a fire event. NFPA 25, as referenced in Rule Chapter 69A-3, F.A.C., shall be utilized to determine if a system condition finding is considered a critical deficiency. In addition, not performing required field service testing of sprinklers shall be considered a critical deficiency.

## Slide 6: FIRE MARSHAL RULES
69A-46.030 Definitions continued.
(b) Noncritical Deficiency. A deficiency that does not have a material effect on the ability of the fire protection system or unit to function in a fire event, but correction is needed to meet the requirements of the standard or for the proper inspection, testing, and maintenance of the system or unit. NFPA 25, as referenced in Rule Chapter 69A-3, F.A.C., shall be utilized to determine if a system-condition finding is considered a noncritical deficiency. In addition, not performing required 3 and 5 year testing requirements shall be considered a noncritical deficiency.
(4) Impairment. A condition causing a fire protection system or unit or portion thereof to be out of order that may result in the fire protection system or unit not functioning in a fire event. NFPA 25, as referenced in Rule Chapter 69A-3, F.A.C., shall be utilized to determine if a system-condition finding is considered an impairment.
Basis of Revision:
NFPA 25, 2011 edition added these definitions when it used the Florida Contractors deficiency lists as the starting point to generate Annex E. This allows the Rule to now match the definitions and classifications in NFPA 25 and allows for better clarity for tagging deficiencies in Florida.

## Slide 7: FIRE MARSHAL RULES
69A-46.035 Standards of the National Fire Protection Association to be Complied With.
The standards of the National Fire Protection Association, which are adopted in Rule Chapter 69A-3, F.A.C., including the editions as adopted therein, shall be complied with by all those holding certificates of competency as fire protection system contractors pursuant to the provisions of Chapter 633, F.S.:
(1) thru (24) deleted
Basis of Revision:
Items 1 thru 24 consisted of the list of NFPA Standards. 69A-3.012 lists the standards and the edition adopted by the state. The listing in this rule was a duplication and this rule does not get updated every three years like 69A-3.012 which can create a conflict between the rules.

## Slide 8: FIRE MARSHAL RULES
69A-46.040 Installation Requirements for Automatic Sprinkler Systems
Employing Water as the Extinguishing Agent.
(6) The contractor whose name appears on the application for the building
permit shall be responsible for the acceptance tests required in NFPA 13. The contractor
or authorized agent shall complete all portions of the Contractor’s Material and Test Certificate(s) that are related to the system being tested. The contractor or authorized agent shall sign and date the test certificates. In cases where there is no building permit, the contractor that supervised the installation shall be responsible for the performance of these duties.
Basis of Revision:
To allow a representative of the actual license holder to sign on his/her behalf
(8) Upon successful completion of acceptance tests, newly installed fire protection systems shall not require a tag until the first inspection occurs in accordance with Rule 69A-46.041, F.A.C.
Basis of Revision:
There is no reason to tag a new system with an inspection tag. The inspection tag is only supposed to be installed or removed by a licensed fire protection contractor or his permitted Water-Based Fire Protection Inspector and no reason to have to send a permitted Water-Based Fire Protection Inspector to install the tag.

## Slide 9: FIRE MARSHAL RULES
69A-46.041 Inspection Requirements for Fire Protection Systems.
(1) A Fire Protection Contractor, contracting to perform inspecting, testing, and maintenance service on a fire protection system shall comply with the requirements of Chapter 633, F.S., and the applicable NFPA 25, Inspection, Testing and Maintenance (ITM) standards, as adopted in Rule Chapter 69A-3, F.A.C. When an inspection/test is required to be performed at a specified frequency up to and including an annual by NFPA 25, all inspection/tests required more frequently than the specified frequency are also required to be performed, e.g., performance of an annual inspection/test would include the inspection/test required on a daily, weekly, monthly, quarterly and semi-annual frequency.
Basis of Revision:
To clarify that the various inspection frequencies are cumulative and not stand alone.

## Slide 10: FIRE MARSHAL RULES
69A-46.041 Inspection Requirements for Fire Protection Systems Continued.
(2) Each system that has been inspected, tested, or maintained by a fire protection contractor, or his or her permitted Water-Based Fire Protection Inspector, shall have a record tag of durable and weather resistant material placed on the system’s main water control valve.
(a) For sprinkler systems, including water spray fixed systems and foam-water sprinkler systems, the main water control valve shall be defined as the valve upstream of the water flow alarm device that controls the entire system.
(b) For standpipe system risers or combination standpipes in a single building, one record tag can be located for all such systems at the main water control valve at the base of the standpipe that is supplying water to all such systems.
(c) For private fire service mains, the main water control valve shall be the first indicating gate valve downstream of the connection to the water source.

## Slide 11: FIRE MARSHAL RULES
69A-46.041 Inspection Requirements for Fire Protection Systems Continued.
(d) Each fire hydrant on a private fire service main shall have a record tag affixed to the hydrant in a manner not to impede operation of the hydrant.
(e) For fire pumps, the main water control valve is defined as the first indicating gate valve downstream of the connection to the water prior to the pump. For multiple fire pumps, one record tag shall be placed at each indicating gate valve prior to each individual fire pump.
(f) For water storage tanks, the main water control valve is defined as the tank discharge valve. For multiple water storage tanks one record tag shall be placed at each tank discharge valve.
(g) For water mist systems, the main water control valve is defined as the first control valve upstream of the water mist system. For multiple water mist systems, one record tag shall be placed at each control valve upstream of each individual system.
Basis of Revision:
To clarify that each individual system and type of system should have a tag and the location of the tag.

## Slide 12: FIRE MARSHAL RULES
69A-46.041 Inspection Requirements for Fire Protection Systems Continued.
(3) Inspection Tags.
(a) After inspection and testing, an inspection tag shall be completed
indicating all work that has been done and then attached to the system’s main
water control valve in such a position as to permit convenient inspection and not
hamper activation or operation. A new inspection tag shall be attached to the
system’s main water control valve each time an inspection and test service is
performed.
Basis of Revision:
To clarify location where tag is to be placed and eliminate the conflict in the rule.

## Slide 13: FIRE MARSHAL RULES
69A-46.041 Inspection Requirements for Fire Protection Systems Continued.
(9) The reverse of the Red or Yellow tag shall include at least four
separate boxes for the listing of repair work as follows:
Basis of Revision:
To have both a Red and Yellow non-compliant tag. The tag colors directly tie into the noncritical, critical and impairment deficiency terms as used in NFPA 25.
(f) Compliance and Non-compliance Tags that are greater than one (1) year old shall be removed from the system except those tags used for three (3) and five (5) year inspection/tests. The Compliance and Non-compliance Tags shall remain on the system until replaced with the next three (3) or five (5) year inspection/test tag. Water-Based Fire Protection Inspectors shall not remove Compliance and Non-Compliance Tags from the system when the tags are less than one (1) year old.
Basis of Revision:
To provide guidance as to how long tags should be maintained on a system which
was not previously included.

## Slide 14: FIRE MARSHAL RULES
69A-46.041 Inspection Requirements for Fire Protection Systems Continued.
(g) A fire protection system that has been repaired to correct
a noted deficiency or impairment documented during an inspection and
test service shall not be required to be reinspected by a Water-Based Fire
Protection Inspector until the next inspection and test scheduled in
accordance with NFPA 25. The repair shall be documented on the reverse
side of the Red or Yellow tag and a retagging of the system shall not be
required.
Basis of Revision:
To clarify that the intent of the rule is to document the repairs on the reverse side of the Red or Yellow tag. A new inspection after the repairs are made and Green tagging the system is not required.

## Slide 15: FIRE MARSHAL RULES
69A-46.041 Inspection Requirements for Fire Protection Systems Continued.
(4) Compliance and Noncompliance Tag.
(a) If a fire protection system is found to be in compliance with the applicable NFPA ITM standards, a GREEN Compliance Tag shall be attached to the main water control valve in such a manner as to be plainly visible and not more than 60 inches above the finished floor. Green tags shall not be placed on a system if deficiencies or impairments still exist from a previous inspection.
Basis of Revision:
To clarify tag location and that you must take into consideration results of a previous inspection when choosing the proper tag.

## Slide 16: FIRE MARSHAL RULES
69A-46.041 Inspection Requirements for Fire Protection Systems Continued.
(b) If a fire protection system is found to have noncritical deficiencies and is not in
compliance with the applicable NFPA ITM standards, a completed YELLOW Noncompliance
Tag shall be attached to the main water control valve of the system to indicate that
corrective action is necessary. The building owner or authorized representative shall be notified by copy of the NFPA 25 inspection report within 30 days of the inspection. If the building owner or authorized representative has not contracted with the inspecting contractor so that the noncritical deficiencies are corrected within 90 days from the date of the inspection, or the inspecting contractor has not received confirmation from the building owner or authorized representative that the corrections have been performed by another licensed Contractor, the authority having jurisdiction shall be notified by the inspecting contractor.
Basis of Revision:
Consistency of tag location with the rule and the addition of a YELLOW tag for non-critical deficiencies. Notification of AHJ if repairs have not been made which will also reduce liability to the contractor since the contractor has notified the AHJ of an issue that requires correction.

## Slide 17: FIRE MARSHAL RULES
69A-46.041 Inspection Requirements for Fire Protection Systems Continued.
(c) If the system has critical deficiencies or is found to be impaired, a completed RED Noncompliance Tag shall be attached to the main water control valve of the system, and the contractor or inspector shall notify the building owner or authorized representative within 24 hours of the time of the inspection. If the building owner or authorized representative has not contracted with the inspecting contractor so that the critical deficiencies are corrected within 30 days from the date of the inspection, or the inspecting contractor has not received confirmation from the building owner or authorized representative that the corrections have been performed by another licensed contractor, the authority having jurisdiction shall be notified by the inspecting contractor. If a system is found to be impaired, the authority having jurisdiction shall be notified within 72 hours of the time of the inspection if the impairment has not been corrected within 72 hours of the finding by the inspecting contractor.
Basis of Revision:
Consistency of tag location with the rule, the specification of a RED tag for critical deficiencies and impairments and notification timeframes to AHJ if repairs have not been made. The notification reduces liability to the contractor since the contractor has notified the AHJ of an issue that requires correction.

## Slide 18: FIRE MARSHAL RULES
69A-46.041 Inspection Requirements for Fire Protection Systems Continued.
(d) If a system is found to have noncritical deficiencies or critical deficiencies, and the building tenant(s) is different from the building owner, the building owner shall notify the tenant(s) within 30 days of receipt of the NFPA 25 inspection report.
Basis of Revision:
Place the responsibility of notification of tenants about inspection/testing deficiencies with the owner in lieu of the inspecting contractor.
(E) If a system is found to have impairments, and the building tenant(s) is different from the building owner, the building owner shall notify the tenant(s) within 72 hours of receiving notification of the impairment.
Basis of Revision:
Place the responsibility of notification of tenants about inspection/testing deficiencies with the owner in lieu of the inspecting contractor.

## Slide 19: FIRE MARSHAL RULES
69A-46.041 Inspection Requirements for Fire Protection Systems Continued.
(5) The contractor shall maintain all records of any fire protection system having been inspected, serviced and maintained as per the applicable NFPA ITM standards. Inspection reports shall be maintained by the contractor for at least 10 years.
Basis of Revision:
Limits the time a contractor has to maintain inspection/test records
(6) These records shall be made available to the State Fire Marshal upon request in the records storage format utilized by the contractor.
Basis of Revision:
Maintains contractors ability to provide requested reports in whatever format the contractor uses.

## Slide 20: FIRE MARSHAL RULES
69A-46.041 Inspection Requirements for Fire Protection Systems Continued.
(7) The inspection report shall be provided to the local Authority Having Jurisdiction (AHJ) in a format mutually determined by the contractor and the AHJ. No other records storage format or transmission method shall be required other than what is required in this rule or NFPA 25.
Basis of Revision:
To assist the contractor from the burden of having to comply with costly systems and multiple different systems. Ensures that reporting is a mutual agreement between AHJ and Contractor.
(10) Pursuant to the provisions of Section 633.312, F.S., it is the owner’s responsibility to maintain the fire protection system and notify the tenant(s) of deficiencies and impairments in accordance with this rule. Affixing an inspection tag as required herein does not eliminate responsibility, nor shall a transfer of risk be construed.
Basis of Revision:
Consistency within the rule as far as transferring responsibility of tenant notification to the owner.

## Slide 21: FIRE MARSHAL RULES
69A-46.041 Inspection Requirements for Fire Protection Systems Continued.
(11) A contractor or licensee that performs ITM services in accordance with the applicable NFPA ITM standards and this rule shall be deemed to have performed to the required standard of care in performing such services.
Basis of Revision:
Will allow a contractor in litigation to demonstrate that they have performed to the industry standard.